{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["UPS ONLINE","Baterias internas de cada UPO"],"not_rendered":{"charts":0,"images":1,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"UPS ONLINE","index":0,"n_rows":29,"n_cols":18,"rows_kept":29,"cut":false,"hidden":false,"merged":[[15,3,15,5],[15,6,15,8],[15,9,15,11],[15,12,15,14],[0,0,0,2],[0,3,0,5],[0,6,0,8],[0,9,0,11],[0,12,0,14],[0,15,0,17],[15,0,15,2]]}
["UPO11-1",null,null,"UPO11-2",null,null,"UPO11-3 ",null,null,"UPO11-1RT/AX",null,null,"UPO11-2RT/AX",null,null,"UPO11-3RT/AX"]
["Potencia (VA)",1000.0,null,"Potencia (VA)",2000.0,null,"Potencia (VA)",3000.0,null,"Potencia (VA)",1000.0,null,"Potencia (VA)",2000.0,null,"Potencia (VA)",3000.0]
["Carga (VA)",1000.0,null,"Carga (VA)",2000.0,null,"Carga (VA)",3000.0,null,"Carga (VA)",1000.0,null,"Carga (VA)",2000.0,null,"Carga (VA)",3000.0]
["Factor de Pot.",0.8,null,"Factor de Pot.",0.8,null,"Factor de Pot.",0.8,null,"Factor de Pot.",0.9,null,"Factor de Pot.",0.9,null,"Factor de Pot.",0.9]
["Factor de Carga",{"$f":"B3/B2","v":1},null,"Factor de Carga",{"$f":"E3/E2","v":1},null,"Factor de Carga",{"$f":"H3/H2","v":1},null,"Factor de Carga",{"$f":"K3/K2","v":1},null,"Factor de Carga",{"$f":"N3/N2","v":1},null,"Factor de Carga",{"$f":"Q3/Q2","v":1}]
["Potencia (W))",500.0,null,"Potencia (W))",300.0,null,"Potencia (W))",1200.0,null,"Potencia (W))",400.0,null,"Potencia (W))",300.0,null,"Potencia (W))",3000.0]
["No Baterías",8.0,null,"No Baterías",12.0,null,"No Baterías",6.0,null,"No Baterías",8.0,null,"No Baterías",30.0,null,"No Baterías",66.0]
["Cap. Bat. (Ah)",9.0,null,"Cap. Bat. (Ah)",9.0,null,"Cap. Bat. (Ah)",9.0,null,"Cap. Bat. (Ah)",9.0,null,"Cap. Bat. (Ah)",7.0,null,"Cap. Bat. (Ah)",9.0]
[]
["Id=",{"$f":"B6/(0.85*B7*10)","v":7.352941176},null,"Id=",{"$f":"E6/(0.85*E7*10)","v":2.941176471},null,"Id=",{"$f":"H6/(0.85*H7*10)","v":23.52941176},null,"Id=",{"$f":"K6/(0.85*K7*10)","v":5.882352941},null,"Id=",{"$f":"N6/(0.85*N7*10)","v":1.176470588},null,"Id=",{"$f":"Q6/(0.85*Q7*10)","v":5.347593583}]
["C=",{"$f":"B10/B8","v":0.8169934641},null,"C=",{"$f":"E10/E8","v":0.3267973856},null,"C=",{"$f":"H10/H8","v":2.614379085},null,"C=",{"$f":"K10/K8","v":0.6535947712},null,"C=",{"$f":"N10/N8","v":0.1680672269},null,"C=",{"$f":"Q10/Q8","v":0.5941770648}]
["(Td)=",{"$f":"B8*60/(B10*SQRT(B11/2+1.05))","v":60.81069095},"minutos","(Td)=",{"$f":"$E$8*60/($E$10*SQRT($E$11/2+1.05))","v":166.6751734},"minutos","(Td)=",{"$f":"H8*60/(H10*SQRT(H11/2+1.05))","v":14.94808081},"minutos","(Td)=",{"$f":"K8*60/(K10*SQRT(K11/2+1.05))","v":78.23618498},"minutos","(Td)=",{"$f":"N8*60/(N10*SQRT(N11/2+1.05))","v":335.2395526},"minutos","(Td)=",{"$f":"Q8*60/(Q10*SQRT(Q11/2+1.05))","v":87.00361478},"minutos"]
["Autonomía =",{"$f":"IF(B12/60>1,INT(B12/60),0)","v":1},"horas","Autonomía =",{"$f":"IF(E12/60>1,INT(E12/60),0)","v":2},"horas","Autonomía =",{"$f":"IF(H12/60>1,INT(H12/60),0)","v":0},"horas","Autonomía =",{"$f":"IF(K12/60>1,INT(K12/60),0)","v":1},"horas","Autonomía =",{"$f":"IF(N12/60>1,INT(N12/60),0)","v":5},"horas","Autonomía =",{"$f":"IF(Q12/60>1,INT(Q12/60),0)","v":1},"horas"]
[null,{"$f":"B12-B13*60","v":0.8106909477},"minutos",null,{"$f":"E12-E13*60","v":46.67517335},"minutos",null,{"$f":"H12-H13*60","v":14.94808081},"minutos",null,{"$f":"K12-K13*60","v":18.23618498},"minutos",null,{"$f":"N12-N13*60","v":35.23955258},"minutos",null,{"$f":"Q12-Q13*60","v":27.00361478},"minutos"]
[]
["UPO22 6  / UPO22 6 RT",null,null,"UPO22-10  / UPO22 10 RT ",null,null,"UPO22-15",null,null,"UPO33-PF365"]
["Potencia (VA)",6000.0,null,"Potencia (VA)",10000.0,null,"Potencia (VA)",15000.0,null,"Potencia (VA)",900000.0]
["Carga (VA)",6000.0,null,"Carga (VA)",9000.0,null,"Carga (VA)",15000.0,null,"Carga (VA)",900000.0]
["Factor de Pot.",0.9,null,"Factor de Pot.",0.9,null,"Factor de Pot.",0.7,null,"Factor de Pot.",0.9]
["Factor de Carga",{"$f":"B18/B17","v":1},null,"Factor de Carga",{"$f":"E18/E17","v":0.9},null,"Factor de Carga",{"$f":"H18/H17","v":1},null,"Factor de Carga",{"$f":"K18/K17","v":1}]
["Potencia (W))",6000.0,null,"Potencia (W))",10000.0,null,"Potencia (W))",15000.0,null,"Potencia (W))",{"$f":"K19*K17*K20","v":810000}]
["No Baterías",20.0,null,"No Baterías",60.0,null,"No Baterías",48.0,null,"No Baterías",17.0]
["Cap. Bat. (Ah)",7.0,null,"Cap. Bat. (Ah)",9.0,null,"Cap. Bat. (Ah)",7.0,null,"Cap. Bat. (Ah)",38.0]
[]
["Id=",{"$f":"B21/(0.85*B22*10)","v":35.29411765},null,"Id=",{"$f":"E21/(0.85*E22*10)","v":19.60784314},null,"Id=",{"$f":"H21/(0.85*H22*10)","v":36.76470588},null,"Id=",{"$f":"K21/(0.85*K22*10)","v":5605.536332}]
["C=",{"$f":"B25/B23","v":5.042016807},null,"C=",{"$f":"E25/E23","v":2.178649237},null,"C=",{"$f":"H25/H23","v":5.25210084},null,"C=",{"$f":"K25/K23","v":147.514114}]
["(Td)=",{"$f":"B23*60/(B25*SQRT(B26/2+1.05))","v":6.297258558},"minutos","(Td)=",{"$f":"$E$23*60/($E$25*SQRT($E$26/2+1.05))","v":18.82892786},"minutos","(Td)=",{"$f":"H23*60/(H25*SQRT(H26/2+1.05))","v":5.95836995},"minutos","(Td)=",{"$f":"K23*60/(K25*SQRT(K26/2+1.05))","v":0.04702690426},"minutos"]
["Autonomía =",{"$f":"IF(B27/60>1,INT(B27/60),0)","v":0},"horas","Autonomía =",{"$f":"IF(E27/60>1,INT(E27/60),0)","v":0},"horas","Autonomía =",{"$f":"IF(H27/60>1,INT(H27/60),0)","v":0},"horas","Autonomía =",{"$f":"IF(K27/60>1,INT(K27/60),0)","v":0},"horas"]
[null,{"$f":"B27-B28*60","v":6.297258558},"minutos",null,{"$f":"E27-E28*60","v":18.82892786},"minutos",null,{"$f":"H27-H28*60","v":5.95836995},"minutos",null,{"$f":"K27-K28*60","v":0.04702690426},"minutos"]

{"sheet":"Baterias internas de cada UPO","index":1,"n_rows":35,"n_cols":7,"rows_kept":35,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[null,"UPS","Cantidad Baterias Orginal"," AH","Baterias X banco Adicional","Maximo de bancos"]
[null,"UPO11-1  (TORRE)",2.0,9.0,6.0,null,"Consultar con Ingeniero de marca los bancos maximos de este modelo"]
[null,"UPO11-2",4.0,9.0," 6 // 12",null,"Consultar con Ingeniero de marca los bancos maximos de este modelo"]
[null,"UPO11-3 ",6.0,9.0," 6 // 12",null,"Consultar con Ingeniero de marca los bancos maximos de este modelo"]
[null,"UPO11-1 AX",3.0,9.0,6.0,"3 Bancos"]
[null,"UPO11-2 AX",6.0,9.0," 6 // 12","3 Bancos"]
[null,"UPO11-3 AX",6.0,9.0,12.0,"3 Bancos"]
[]
[null,"UPO11-1 RT ",2.0,9.0,6.0,null,"Consultar con Ingeniero de marca los bancos maximos de este modelo"]
[null,"UPO11-2 RT ",4.0,9.0," 6 // 12",null,"Consultar con Ingeniero de marca los bancos maximos de este modelo"]
[null,"UPO11-3 RT ",6.0,null," 6 // 12",null,"Consultar con Ingeniero de marca los bancos maximos de este modelo"]
[null,"UPO11-1 RT AX",2.0,9.0,6.0,"3 Bancos"]
[null,"UPO11-2 RT AX",4.0,9.0,8.0,"3 Bancos"]
[null,"UPO11-3 RT AX",6.0,9.0,12.0,"3 Bancos"]
[]
[null,"UPO22-6",20.0,7.0,40.0,"3 Bancos"]
[null,"UPO22-10",20.0,9.0,40.0,"3 Bancos"]
[null,"UPO22-6 RT",20.0,7.0,20.0,"5 Bancos"]
[null,"UPO22-10 RT",20.0,9.0,20.0,"5 Bancos"]
[null,"UPO22-15",48.0,7.0,48.0,"4 Bancos"]
[]
[null,"UPO33-20 ",17.0,38.0,17.0,"4 Bancos"]
[null,"UPO33-30",17.0,38.0,17.0,"4 Bancos"]
[null,"UPO33-40",17.0,65.0,17.0,"4 Bancos"]
[null,"UPO33-60",17.0,100.0,17.0,"4 Bancos"]
[null,"UPO33-80",40.0,65.0,40.0,"4 Bancos"]
[null,"UPO33-100",40.0,65.0,40.0,"4 Bancos"]
[null,"UPO33-120",40.0,100.0,40.0,"4 Bancos"]
[null,"UPO33-160",40.0,100.0,40.0,"4 Bancos"]
[null,"UPO33-200",40.0,100.0,40.0,"4 Bancos"]